## EPA ID 1 20MW Boiler Opacity
AKD NSW Pty Ltd (Tumut Sawmill), Adelong Road, Tumut 2720 - EPL# 63
Link to EPA Public Registers https://www.epa.nsw.gov.au/licensing-and-regulation/public-registers
EPA ID 1 20MW Boiler Stack. Continuous opacity monitoring required
Date Sampled. | Date Data Obtained* | Date Published | Smoke Emissions (percent opacity) |  |  | Notes | Correction Log
Limit 20% opacity
|  |  | Lowest Value | Mean Value | Highest Value |  | Description | Date
Where no data has been published for a particular month it indicates the level of pollutant was below the level of detection or there was no discharge for that month
*Data is considered "Obtained" once the following is completed. 1. the pollutant is sampled 2. the sample is analysed producing a numeric result 3. the licensee receives the sample monitoring results 4. the monitoring results are standardised where required so that they are expressed in the form required by the monitoring condition.
2025-05-02 | 2025-06-06 | 2025-06-10 | 0 | 6.24 | 66.2 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler demand (load) reduced at times throughout the month.
2025-04-02 | 2025-06-06 | 2025-06-10 | 0 | 6.96 | 73.2 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler demand (load) reduced at times throughout the month.
2025-03-03 | 2025-06-06 | 2025-06-10 |  | 8.09 | 77.8 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler demand (load) reduced at times throughout the month.
2025-02-01 | 2025-03-03 | 2025-03-03 | 0 | 9.81 | 83 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler demand (load) reduced at times throughout the month.
2025-01-02 | 2025-02-22 | 2025-02-22 | 0 | 3.79 | 64 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. -
2024-12-01 | 2025-02-22 | 2025-02-22 | 0 | 7.59 | 61 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-11-01 | 2025-02-22 | 2025-02-22 | 0 | 9.89 | 78 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-10-01 | 2024-11-12 | 2024-11-12 | 0 | 11.58 | 67 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-09-01 | 2024-10-10 | 2024-10-10 | 0 | 11.54 | 68 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-08-01 | 2024-09-02 | 2024-09-02 | 0 | 11.41 | 70 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-07-01 | 2024-08-06 | 2024-08-06 | 0 | 12.29 | 68 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-06-01 | 2024-07-08 | 2024-07-08 | 0 | 12.65 | 69 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-05-01 | 2024-06-13 | 2024-06-13 | 0 | 13.16 | 68 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-04-01 | 2024-05-14 | 2024-05-14 | 0 | 11.45 | 74 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-03-01 | 2024-04-19 | 2024-04-19 | 0 | 11.8 | 76 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. | Data corruption issue obtained and published 19/4/24
2024-02-01 | 2024-04-19 | 2024-04-19 | 0 | 11.99 | 74 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. | Data corruption issue obtained and published 19/4/24
2024-01-01 | 2024-04-19 | 2024-04-19 | 0 | 8.44 | 76 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. Boiler shut down over xmas break for an extended period | Data corruption issue obtained and published 19/4/24
2023-12-01 | 2024-04-19 | 2024-04-19 | 0 | 5.52 | 68 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. Boiler shut down over xmas break for an extended period | Data corruption issue obtained and published 19/4/24
2023-11-01 | 2024-04-19 | 2024-04-19 | 0 | 10.54 | 64 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. | Data corruption issue obtained and published 19/4/24
2023-10-01 | 2024-04-19 | 2024-04-19 | 0 | 14.13 | 71 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. | Data corruption issue obtained and published 19/4/24
2023-09-01 | 2024-04-19 | 2024-04-19 | 0 | 8.92 | 74 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. | Data corruption issue obtained and published 19/4/24
2023-08-01 | 2024-04-19 | 2024-04-19 | 0 | 12.1 | 86 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month. | Data corruption issue obtained and published 19/4/24
2023-07-01 | 2023-08-25 | 2023-08-25 | 0 | 11.52 | 89 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-06-01 | 2023-08-25 | 2023-08-25 | 0 | 11.33 | 89 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-05-01 | 2023-06-09 | 2023-06-09 | 0 | 10.3 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-04-01 | 2023-06-08 | 2023-06-08 | 0 | 11.8 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-03-01 | 2023-04-05 | 2023-04-05 | 0 | 13.14 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-02-01 | 2023-04-05 | 2023-04-05 | 0 | 11.93 | 85 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2023-01-01 | 2023-04-05 | 2023-04-05 | 0 | 11.6 | 91 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Plant restarted 8th Jan 2023 after full site shut down and slowly brought up to temperature.
2022-12-01 | 2023-04-05 | 2023-04-05 | 0 | 9.24 | 90 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Plant Shut down 22/12/22 for annual xmas shut period.
2022-11-01 | 2023-01-11 | 2023-01-11 | 0 | 10.93 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. 3 days of data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2022-10-01 | 2022-11-30 | 2022-11-30 | 0 | 14.34 | 83 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Excursion this month included period after extended shut and cold start-up.
2022-09-01 | 2022-11-30 | 2022-11-30 | 0 | 13.4 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2022-08-01 | 2022-09-13 | 2022-09-13 | 0 | 15.59 | 88 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2022-07-01 | 2022-09-13 | 2022-09-13 | 0 | 13.38 | 92 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2022-06-01 | 2022-07-06 | 2022-07-06 | 0 | 13.95 | 86 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2022-05-01 | 2022-06-13 | 2022-06-13 | 0 | 13.5 | 76 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2022-04-01 | 2022-05-26 | 2022-05-26 | 0 | 6.92 | 69 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2022-03-01 | 2022-05-26 | 2022-05-26 | 0 | 0 | 0 | The data is continually monitored and logged for operational purposes but a programming issue results in data corruption so reporting not possible.
2022-02-01 | 2022-05-26 | 2022-05-26 | 0 | 12.15 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2022-01-01 | 2022-02-22 | 2022-02-22 | 0 | 12.3 | 77 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-12-01 | 2022-05-26 | 2022-05-26 | 0 | 0 | 0 | The data is continually monitored and logged for operational purposes but a programming issue results in data corruption so reporting not possible.
2021-11-01 | 2021-12-08 | 2021-12-09 | 0 | 14.3 | 90 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-10-01 | 2021-12-08 | 2021-12-09 | 0 | 15.2 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-09-01 | 2021-12-08 | 2021-12-09 | 0 | 17.03 | 65 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-08-01 | 2021-12-08 | 2021-12-09 | 0 | 24.35 | 81 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-07-01 | 2021-12-08 | 2021-12-09 | 0 | 18.28 | 87 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-06-01 | 2021-07-07 | 2021-07-13 | 0 | 17.9 | 98 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2021-05-01 | 2021-06-28 | 2021-06-28 | 0 | 16.76 | 84 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2021-04-01 | 2021-05-21 | 2021-05-21 | 0 | 12.8 | 86 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2021-03-01 | 2021-05-21 | 2021-05-21 | 0 | 12.6 | 82 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2021-02-01 | 2021-03-25 | 2021-03-25 | 0 | 9.2 | 71 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2021-01-01 | 2021-03-25 | 2021-03-25 | 0 | 9.5 | 94 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-12-01 | 2021-01-19 | 2021-01-20 | 0 | 8.46 | 78 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-11-01 | 2021-01-19 | 2021-01-20 | 0 | 12.15 | 91 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-10-01 | 2020-11-14 | 2020-11-23 | 0 | 19.24 | 82 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-09-01 | 2020-10-07 | 2020-10-08 | 0 | 19.45 | 81 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-08-01 | 2020-10-01 | 2020-10-08 | 0 | 19.25 | 88 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
20/8/20 - Additional column and note added to clarify date sampling data was obtained.
2020-07-01 |  |  | 0 | 17.51 | 85 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-06-01 |  |  | 0 | 17.67 | 82 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-05-01 |  |  | 0 | 16.24 | 77 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-04-01 |  |  | 0 | 15.3 | 85 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-03-01 |  |  | 0 | 15.55 | 80 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-02-01 |  |  | 0 | 13.8 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2020-01-01 |  |  | 0 | 3.9 | 92 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Plant restarted on the 22nd Jan 2020 after annual shutdown.
2019-12-01 |  |  | 6 | 7.35 | 94 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Plant shut down 22/12/19 for annual xmas shut period.
2019-11-01 |  |  | 0 | 9.2 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-10-01 |  |  | 0 | 8.53 | 94 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-09-01 |  |  | 0 | 15.46 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-08-01 |  |  | 0 | 17.68 | 80 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-07-01 |  |  | 0 | 22.1 | 86 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-06-01 |  |  | 0 | 20.03 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-05-01 |  |  | 0 | 16.79 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-04-01 |  |  | 0 | 13.93 | 94 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-03-01 |  |  | 0 | 14.22 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-02-01 |  |  | 0 | 13.93 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2019-01-01 |  |  | 0 | 8.2 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2018-12-01 |  |  | 0 | 14.05 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. One larger excursion of 20-30 min after breakdown. Mean value is best indicator of plant performance.
2018-11-01 |  |  | 0 | 11.41 | 87 | Restart and adjustment of fuel mix. Excursions generally of 5 min duration
2018-10-01 |  |  | 0 | 15.39 | 71 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2018-09-01 |  |  | 0 | 20.37 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2018-08-01 |  |  | 0 | 22.79 | 84 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance.
2018-07-01 |  |  | 0 | 23.34 | 98
2018-06-01 |  |  | 0 | 20.59 | 98
2018-05-01 |  |  | 0 | 20.2 | 98 |  | Update table to conform with current guidelines | 26/6/2018
2018-04-01 |  |  | 0 | 16.35 | 94
2018-03-01 |  |  | 0 | 17.07 | 95
2018-02-01 |  |  | 0 | 18.96 | 96
2018-01-01 |  |  | 0 | 12.17 | 94
2017-12-01 |  |  | 0 | 11.14 | 96
2017-11-01 |  |  | 0 | 15.68 | 98
2017-10-01 |  |  | 0 | 17.24 | 98
2017-09-01 |  |  | 0 | 20.53 | 98
2017-08-01 |  |  | 0 | 19.67 | 98
2017-07-01 |  |  | 0 | 19.81 | 96
2017-06-01 |  |  | 0 | 9.92 | 78
2017-06-01 |  |  | 0 | 19.94 | 94
2017-05-01 |  |  | 0 | 8.73 | 99
2017-05-01 |  |  | 0 | 19.95 | 94
2017-04-01 |  |  | 0 | 16.26 | 90
2017-03-01 |  |  | 0 | 16.99 | 98
2017-02-01 |  |  | 0 | 19.5 | 91
2017-01-01 |  |  | -25 | 12.18 | 98
2016-12-01 |  |  | -2 | 12.68 | 96
2016-11-01 |  |  | -1 | 16.42 | 96
2016-10-01 |  |  | -2 | 16.94 | 96
2016-09-01 |  |  | -1 | 16.97 | 96
2016-08-01 |  |  | 0 | 7.1 | 100
2016-08-01 |  |  | 0 | 17.93 | 92
2016-07-01 |  |  | 0 | 18.4 | 98
2016-06-01 |  |  | -2 | 19.2 | 90
2016-05-01 |  |  | 0 | 20.55 | 92
2016-04-01 |  |  | 0 | 15.9 | 91
2016-03-01 |  |  | 0 | 16.6 | 96
2016-02-01 |  |  | 0 | 16.3 | 96
2016-01-01 |  |  | 0 | 12.49 | 95
2015-12-01 |  |  | 0 | 8.94 | 79
2015-11-01 |  |  | 0 | 13.62 | 74
2015-10-01 |  |  | 0 | 16.44 | 98
2015-09-01 |  |  | 0 | 16.19 | 92
2015-08-01 |  |  | 0 | 17.6 | 90
2015-07-01 |  |  | 0 | 16.79 | 98
2015-06-01 |  |  | 0 | 18.5 | 94
2015-05-01 |  |  | 0 | 17.01 | 98
2015-04-01 |  |  | 0 | 15.26 | 81
2015-03-01 |  |  | 0 | 20.56 | 91
2015-02-01 |  |  | 0 | 20.14 | 86
2015-01-01 |  |  | 0 | 7.69 | 89
2014-12-01 |  |  | 0 | 6.62 | 92
2014-11-01 |  |  | 0 | 12.53 | 99
2014-10-01 |  |  | 0 | 15.4 | 100
2014-09-01 |  |  | 0 | 7.45 | 100

## EPA ID 1 20MW Boiler Stack
AKD NSW Pty Ltd (Tumut Sawmill), Adelong Road, Tumut 2720 - EPL# 63
Link to EPA Public Registers https://www.epa.nsw.gov.au/licensing-and-regulation/public-registers
EPA ID 1 20MW Boiler Stack. Annual stack test required
Date Sampled. | Date Data Obtained* | Date Published | Particulate Matter (mg/m3) |  |  | Notes | Correction Log
100 percentile Limit. 175 mg/m3
|  |  | Lowest Value | Mean Value | Highest Value |  | Description | Date
Where no data has been published for a particular month it indicates the level of pollutant was below the level of detection or there was no discharge for that month
*Data is considered "Obtained" once the following is completed. 1. the pollutant is sampled 2. the sample is analysed producing a numeric result 3. the licensee receives the sample monitoring results 4. the monitoring results are standardised where required so that they are expressed in the form required by the monitoring condition.
2025-04-01 | 2025-06-01 | 2025-06-01 | 160 | 160 | 160 | Compliance with Licence Limit. Reduced load throughout the reporting period.
2024-04-11 | 2024-05-14 | 2024-05-15 | 370 | 370 | 370 | EPL licence limit exceeded for the 100% capacity test.
2023-05-01 | 2023-06-01 | 2023-06-01 | 240 | 240 | 240 | EPL licence limit exceeded for the 100% capacity test.
2022-03-01 | 2022-05-01 | 2022-05-01 | 350 | 350 | 350 | EPL licence limit exceeded for the 100% capacity test.
2021-01-28 | 2021-05-21 | 2021-06-01 | 260 | 260 | 260 | EPL licence limit exceeded for the 100% capacity test.
20/8/20 - Additional column and note added to clarify date sampling data was obtained.
2020-01-01 |  |  | 220 | 220 | 230 | 100% capacity test.
2019-02-01 |  |  | 120 | 120 | 120 | 100% capacity test.
2017-10-01 |  |  | 250 | 250 | 250 |  | Update table to conform with current guidelines | 26/6/2018
2017-04-01 |  |  | 230 | 240 | 250
2015-03-01 |  |  | 220 | 220 | 220

## EPD ID 2 10MW Boiler Opacity
AKD NSW Pty Ltd (Tumut Sawmill), Adelong Road, Tumut 2720 - EPL# 63
Link to EPA Public Registers https://www.epa.nsw.gov.au/licensing-and-regulation/public-registers
EPA ID 2 10MW Boiler Stack. Continuous opacity monitoring required
Date Sampled. | Date Data Obtained* | Date Published | Smoke Emissions (percent opacity) |  |  | Notes | Correction Log
Limit 20% opacity
|  |  | Lowest Value | Mean Value | Highest Value |  | Description | Date
Where no data has been published for a particular month it indicates the level of pollutant was below the level of detection or there was no discharge for that month
*Data is considered "Obtained" once the following is completed. 1. the pollutant is sampled 2. the sample is analysed producing a numeric result 3. the licensee receives the sample monitoring results 4. the monitoring results are standardised where required so that they are expressed in the form required by the monitoring condition.
2025-05-01 | 2025-06-06 | 2025-06-10 | 0 | 0 | 0 | No data logged for reporting purposes this month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2025-04-01 | 2025-06-06 | 2025-06-10 | 0 | 0 | 0 | No data logged for reporting purposes this month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2025-03-01 | 2025-06-06 | 2025-06-10 | 0 | 0 | 0 | No data logged for reporting purposes this month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2025-02-01 | 2025-03-03 | 2025-03-03 | 0 | 3.93 | 55 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode for extended periods throughout the month.
2025-01-02 | 2025-02-02 | 2025-02-02 | 0 | 4.2 | 78 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-12-01 | 2025-02-02 | 2025-02-02 | 0 | 6.95 | 60 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-11-01 | 2025-02-02 | 2025-02-02 | 0 | 5.3 | 78 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-10-01 | 2024-11-12 | 2024-11-12 | 0 | 6.9 | 65 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-09-01 | 2024-10-10 | 2024-10-10 | 0 | 7.09 | 74 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-08-01 | 2024-09-02 | 2024-09-02 | 0 | 8.76 | 80 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-07-01 | 2024-08-06 | 2024-08-06 | 0 | 6.06 | 74 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-06-01 | 2024-07-08 | 2024-07-08 | 0 | 8.76 | 63 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-05-01 | 2024-06-13 | 2024-06-13 | 0 | 8.61 | 76 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-04-01 | 2024-05-14 | 2024-05-14 | 0 | 7.75 | 75 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-03-01 | 2024-04-19 | 2024-04-19 | 0 | 7.9 | 78 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-02-01 | 2024-04-19 | 2024-04-19 | 0 | 5.7 | 72 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2024-01-01 | 2024-04-19 | 2024-04-19 | 0 | 2.6 | 69 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-12-01 | 2024-04-19 | 2024-04-19 | 0 | 2.9 | 42 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-11-01 | 2024-04-19 | 2024-04-19 | 0 | 5.3 | 81 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-10-01 | 2024-04-19 | 2024-04-19 | 0 | 4.5 | 67 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-09-01 | 2024-04-19 | 2024-04-19 | 0 | 10.5 | 100 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-08-01 | 2024-04-19 | 2024-04-19 | 0 | 11.3 | 83 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-07-01 | 2023-08-25 | 2023-08-25 | 0 | 14.3 | 94 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-06-01 | 2023-08-25 | 2023-08-25 | 5 | 12.74 | 96 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-05-01 | 2023-06-09 | 2023-06-09 | 5 | 11.3 | 92 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-04-01 | 2023-06-08 | 2023-06-08 | 0 | 11.2 | 99 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-03-01 | 2023-04-05 | 2023-04-05 | 0 | 9.74 | 98 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5 min duration. Mean value is best indicator of plant performance. Boiler shut down (controlled) or run in low fire mode due to a lack of product throughout the month.
2023-02-01 | 2023-04-05 | 2023-04-05 | 2 | 8.66 | 70 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2023-01-01 | 2023-04-05 | 2023-04-05 | 0 | 7.38 | 95 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Plant restarted 8th Jan 2023 after full site shut down and slowly brought up to temperature.
2022-12-01 | 2023-04-05 | 2023-04-05 | 0 | 4.37 | 89 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Plant Shut down 22/12/22 for annual xmas shut period.
2022-11-01 | 2023-04-05 | 2023-04-05 | 0 | 5.92 | 99 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. 3 days of data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2022-10-01 | 2023-04-05 | 2023-04-05 | 0 | 8.53 | 97 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2022-09-01 | 2023-04-05 | 2023-04-05 | 0 | 6.7 | 79 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2022-08-01 | 2023-04-05 | 2023-04-05 | 0 | 5.83 | 81 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2022-07-01 | 2023-04-05 | 2023-04-05 | 0 | 6.68 | 73 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2022-06-01 | 2023-04-05 | 2023-04-05 | 0 | 5.8 | 84 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2022-05-01 | 2023-04-05 | 2023-04-05 | 0 | 6.8 | 57 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2022-04-01 | 2023-04-05 | 2023-04-05 | 0 | 6.92 | 69 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance.
2022-03-01 | 2023-04-05 | 2023-04-05 | 0 | 0 | 0 | The data is continually monitored and logged for operational purposes but a programming issue results in data corruption so reporting not possible.
2022-02-01 | 2023-04-05 | 2023-04-05 | 0 | 5.92 | 62 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2022-01-01 | 2023-04-05 | 2023-04-05 | 0 | 6.9 | 99 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-12-01 | 2023-04-05 | 2023-04-05 | 0 | 0 | 0 | The data is continually monitored and logged for operational purposes but a programming issue results in data corruption so reporting not possible.
2021-11-01 | 2023-04-05 | 2023-04-05 | 0 | 6.5 | 64 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-10-01 | 2023-04-05 | 2023-04-05 | 0 | 6.89 | 98 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-09-01 | 2023-04-05 | 2023-04-05 | 0 | 7.04 | 60 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-08-01 | 2023-04-05 | 2023-04-05 | 0 | 8.02 | 92 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-07-01 | 2023-04-05 | 2023-04-05 | 0 | 8.6 | 79 | Excursion due to boiler clean, restart and adjustment of fuel mix. Generally 5-10 min duration. Mean value is best indicator of plant performance. Significant data loss occurred during the reporting month. The data is continually monitored and logged for operational purposes but a programming issue results in data corruption. issue on-going.
2021-06-01 | 2023-04-05 | 2023-04-05 | 0 | 4.65 | 99 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2021-05-01 | 2023-04-05 | 2023-04-05 | 0 | 4.97 | 86 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2021-04-01 | 2023-04-05 | 2023-04-05 | 0 | 6.45 | 63 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2021-03-01 | 2023-04-05 | 2023-04-05 | 7 | 15 | 75 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2021-02-01 | 2023-04-05 | 2023-04-05 | 5 | 11.06 | 73 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2021-01-01 | 2023-04-05 | 2023-04-05 | 2 | 11.3 | 70 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-12-01 | 2023-04-05 | 2023-04-05 | 1 | 5.76 | 65 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-11-01 | 2023-04-05 | 2023-04-05 | 0 | 7.9 | 62 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-10-01 | 2023-04-05 | 2023-04-05 | 0 | 9.22 | 76 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-09-01 | 2023-04-05 | 2023-04-05 | 0 | 8.89 | 57 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-08-01 | 2023-04-05 | 2023-04-05 | 0 | 9.05 | 70 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
20/8/20 - Additional column and note added to clarify date sampling data was obtained.
2020-07-01 |  |  | 0 | 9.23 | 92 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-06-01 |  |  | 0 | 10.18 | 85 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-05-01 |  |  | 0 | 9.6 | 72 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-04-01 |  |  | 3 | 9.6 | 97 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-03-01 |  |  | 0 | 14.45 | 78 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-02-01 |  |  | 12 | 17.8 | 96 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2020-01-01 |  |  | 0 | 12.1 | 79 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance. Plant restarted on the 6th Jan after annual shutdown period.
2019-12-01 |  |  | 0 | 12.64 | 84 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance. Plant shut down 22nd Dec 2019 for annual xmas shutdown.
2019-11-01 |  |  | 0 | 11.6 | 93 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-10-01 |  |  | 0 | 6.24 | 88 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-09-01 |  |  | 0 | 9.71 | 99 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-08-01 |  |  | 0 | 8.46 | 64 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-07-01 |  |  | 1 | 9.41 | 91 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-06-01 |  |  | 0 | 9.04 | 57 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-05-01 |  |  | 0 | 7.88 | 59 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-04-01 |  |  | 0 | 9.08 | 78 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-03-01 |  |  | 0 | 8.2 | 86 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-02-01 |  |  | 0 | 8.06 | 98 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2019-01-01 |  |  | 0 | 6.7 | 81 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2018-12-01 |  |  | 0 | 8.46 | 93 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2018-11-01 |  |  | 0 | 7.84 | 99 | Adjustment of fuel mix. Excursion generally <5 min duration.
2018-10-01 |  |  | 0 | 7.36 | 69 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2018-09-01 |  |  | 0 | 8.71 | 93 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2018-08-01 |  |  | 1 | 9.38 | 93
2018-07-01 |  |  | 0 | 10.24 | 89 | Excursions due to restart of boiler after cleaning - Generally 5 min duration. Mean value is best indicator of plant performance.
2018-06-01 |  |  | 0 | 9.76 | 100
2018-05-01 |  |  | 0 | 8.58 | 100 |  | Update table to conform with current guidelines | 26/6/2018
2018-04-01 |  |  | 0 | 7.21 | 94
2018-03-01 |  |  | 0 | 8.29 | 99
2018-02-01 |  |  | 0 | 8.25 | 99
2018-01-01 |  |  | 0 | 6.57 | 100
2017-12-01 |  |  | 0 | 6.31 | 96
2017-11-01 |  |  | 0 | 8.5 | 100
2017-10-01 |  |  | 0 | 7.6 | 100
2017-09-01 |  |  | 0 | 8.86 | 100
2017-08-01 |  |  | 0 | 8.63 | 100
2017-07-01 |  |  | 0 | 9.42 | 81
2017-06-01 |  |  | 0 | 9.92 | 78
2017-05-01 |  |  | 0 | 8.73 | 99
2017-04-01 |  |  | 0 | 8.21 | 99
2017-03-01 |  |  | 0 | 7.09 | 100
2017-02-01 |  |  | 0 | 8.07 | 81
2017-01-01 |  |  | 0 | 5.67 | 100
2016-12-01 |  |  | 0 | 5.41 | 79
2016-11-01 |  |  | 0 | 6.15 | 99
2016-10-01 |  |  | 0 | 6.18 | 98
2016-09-01 |  |  | 0 | 7.01 | 97
2016-08-01 |  |  | 0 | 7.1 | 100
2016-07-01 |  |  | 0 | 7 | 100
2016-06-01 |  |  | 0 | 7.12 | 98
2016-05-01 |  |  | 0 | 6 | 54
2016-04-01 |  |  | 0 | 5.9 | 95
2016-03-01 |  |  | 0 | 6.1 | 80
2016-02-01 |  |  | 0 | 5.9 | 99
2016-01-01 |  |  | 0 | 5.74 | 86
2015-12-01 |  |  | 0 | 3.44 | 81
2015-11-01 |  |  | 0 | 5.37 | 43
2015-10-01 |  |  | 0 | 6.32 | 100
2015-09-01 |  |  | 0 | 6.18 | 74
2015-08-01 |  |  | 0 | 6.16 | 86
2015-07-01 |  |  | 0 | 7.3 | 100
2015-06-01 |  |  | 0 | 7.97 | 99
2015-05-01 |  |  | 0 | 7.67 | 100
2015-04-01 |  |  | 0 | 8.33 | 72
2015-03-01 |  |  | 0 | 6.25 | 81
2015-02-01 |  |  | 0 | 6.45 | 96
2015-01-01 |  |  | 0 | 23.7 | 88
2014-12-01 |  |  | 0 | 13.59 | 73
2014-11-01 |  |  | 0 | 20.8 | 95
2014-10-01 |  |  | 0 | 16.5 | 100
2014-09-01 |  |  | 0 | 16.68 | 98

## EPA ID 2 10 MW Boiler Stack
AKD NSW Pty Ltd (Tumut Sawmill), Adelong Road, Tumut 2720 - EPL# 63
Link to EPA Public Registers https://www.epa.nsw.gov.au/licensing-and-regulation/public-registers
EPA ID 2 10MW Boiler Stack. Annual stack test required
Date Sampled. | Date Data Obtained* | Date Published | Particulate Matter (mg/m3) |  |  | Notes | Correction Log
100 percentile Limits. 150 mg/m3
|  |  | Lowest Value | Mean Value | Highest Value |  | Description | Date
Where no data has been published for a particular month it indicates the level of pollutant was below the level of detection or there was no discharge for that month
*Data is considered "Obtained" once the following is completed. 1. the pollutant is sampled 2. the sample is analysed producing a numeric result 3. the licensee receives the sample monitoring results 4. the monitoring results are standardised where required so that they are expressed in the form required by the monitoring condition.
2025-04-01 | 2025-06-01 | 2025-06-01 | 120 | 120 | 120 | Compliance with Licence Limit. Reduced load throughout the reporting period.
2024-04-11 | 2024-05-14 | 2024-05-15 | 170 | 170 | 170 | EPL licence limit exceeded for the 100% capacity test.
2023-04-01 | 2023-04-01 | 2023-06-01 | 240 | 240 | 240 | EPL licence limit exceeded for the 100% capacity test.
2022-03-01 | 2022-05-01 | 2022-05-01 | 270 | 270 | 270 | EPL licence limit exceeded for the 100% capacity test.
2021-01-01 | 2021-05-01 | 2021-06-01 | 170 | 170 | 170 | EPL licence limit exceeded for the 100% capacity test.
20/8/20 - Additional column and note added to clarify date sampling data was obtained.
2020-01-01 |  |  | 110 | 140 | 150 | 100% capacity test
2019-02-01 |  |  | 150 | 150 | 150 | 100% capacity test
2017-10-01 |  |  | 170 | 180 | 190 |  | Data corrected to reflect final analysis report dated 31 January 2018 | 2018-05-22
2017-04-01 |  |  | 220 | 240 | 250
2015-03-01 |  |  | 160 | 160 | 160

## EPA ID 5 Water Treatment Plant
AKD NSW Pty Ltd (Tumut Sawmill). Adelong Road, Tumut, NSW 2720 EPL# 63
Link to EPA Public Registers https://www.epa.nsw.gov.au/licensing-and-regulation/public-registers
EPA ID 5 Discharge pipe for stormwater treatment plant. Monthly during discharge sample required
Date Sampled. | Date Data Obtained* | Date Published | Conductivity (microsiemens/cm) |  |  | pH | Total Suspended Solids (mg/L) |  |  | Biochemical Oxygen Demand (mg/L) |  |  | Oil & Grease (mg/L) |  |  | Notes | Correction Log
|  |  | No Limit |  |  | Limit 6.5 - 8.5 | Limit 50 mg/L |  |  | Limit 40 mg/L |  |  | Limit 10 mg/L
|  |  | Lowest Value | Mean Value | Highest Value | Result | Lowest Value | Mean Value | Highest Value | Lowest Value | Mean Value | Highest Value | Lowest Value | Mean Value | Highest Value |  | Description | Date
Where no data has been published for a particular month it indicates the level of pollutant was below the level of detection or there was no discharge for that month
*Data is considered "Obtained" once the following is completed. 1. the pollutant is sampled 2. the sample is analysed producing a numeric result 3. the licensee receives the sample monitoring results 4. the monitoring results are standardised where required so that they are expressed in the form required by the monitoring condition.
2025-04-25 | 2025-06-06 | 2025-06-10 | 1940 | 1940 | 1940 | 8.1 | 62 | 62 | 62 | 17 | 17 | 17 | 2 | 2 | 2 | no discharge from dam. Water recovered for reuse. Sample recorded but not reported in annual return due to no discharge.
2025-01-14 | 2025-02-20 | 2025-02-20 | 534 | 534 | 534 | 7.2 | 80 | 80 | 80 | 17 | 17 | 17 | 1 | 1 | 1 | Sample result added to sheet for completeness. Wet weather bypass>10mm previous 24 hrs - (12 mm) Sample recorded but not reported annually.
2024-09-26 | 2024-11-11 | 2024-11-11 | 244 | 244 | 244 | 7 | 250 | 250 | 250 | 34 | 34 | 34 | 2 | 2 | 2 | Sample result added to sheet for completeness. Wet weather bypass>10mm previous 24 hrs - (24.8 mm) Sample recorded but not reported annually.
2024-08-14 | 2024-11-11 | 2024-11-11 | 427 | 427 | 427 | 8.1 | 12 | 12 | 12 | 19 | 19 | 19 | 4 | 4 | 4 | First result for a number of months. Drizzle rain in prev 24 hrs 0.4mm. Water recycled to plant. Rain on day of sample 17.4 mm. To be reported in Annual return.
2024-07-09 | 2024-08-06 | 2024-08-06 | 423 | 423 | 423 | 8.3 | 247 | 247 | 247 | 41 | 41 | 41 | 2 | 2 | 2 | Sample result added to sheet for completeness. Wet weather bypass>10mm previous 24 hrs - (18.2mm) Sample recorded but not reported annually.
2023-07-05 | 2023-07-27 | 2023-07-27 | 380 | 380 | 380 | 6.7 | 390 | 390 | 390 | 45 | 45 | 45 | 2 | 2 | 2 | no discharge from dam. Water recovered for reuse. Sample recorded but not reported in annual return due to no discharge.
2023-06-08 | 2023-06-23 | 2023-06-23 | 395 | 395 | 395 | 8 | 49 | 49 | 49 | 32 | 32 | 32 | 4 | 4 | 4 | discharge from dam to creek. Water processed. First discharge for a number of months.
2023-02-14 | 2023-04-05 | 2023-04-05 | 372 | 372 | 372 | 6.6 | 57 | 57 | 57 | 35 | 35 | 35 | 3 | 3 | 3 | First result for a number of months. Drizzle rain in prev 24 hrs. Water recycled to plant. To be reported in Annual return.
2022-11-01 | 2022-11-30 | 2022-11-30 | 247 | 247 | 247 | 6.5 | 145 | 145 | 145 | 48 | 48 | 48 | 2 | 2 | 2 | First result for a number of months.15mm rain. Wet weather bypass>10mm. Sample recorded but not reported in annual return.
2022-09-27 | 2023-04-05 | 2023-04-05 | 205 | 205 | 205 | 6.6 | 19 | 19 | 19 | 11 | 11 | 11 | 2 | 2 | 2 | Compliant flow sample for reporting purposes.
2022-08-01 | 2022-09-13 | 2022-09-13 | 246 | 246 | 246 | 6.5 | 130 | 130 | 130 | 50 | 50 | 50 | 4 | 4 | 4 | Compliant flow sample for reporting purposes. TSS well above limit. BOD over limit. No discharge from site (recycled into process).
2022-06-06 | 2022-07-06 | 2022-07-06 | 158 | 158 | 158 | 8 | 310 | 310 | 310 | 28 | 28 | 28 | 1 | 1 | 1 | Compliant flow sample for reporting purposes. TSS well above limit. No discharge from site (recycled into process).
2022-04-20 | 2022-06-26 | 2022-06-26 | 320 | 320 | 320 | 7.6 | 132 | 132 | 132 | 60 | 60 | 60 | 3 | 3 | 3 | First result for a number of months.32mm rain. Wet weather bypass>10mm. Sample recorded but not reported in annual return.
2022-01-06 | 2022-02-22 | 2022-02-22 | 204 | 204 | 204 | 6.4 | 32 | 32 | 32 | 40 | 40 | 40 | 4 | 4 | 4 | Slightly below pH limit. Not Field measured. 9.8 mm rain on the day of sample so compliant test for reporting purposes. | Added rainfall data. | 2022-05-26
2021-10-14 | 2021-12-08 | 2021-12-09 | 264 | 264 | 264 | 7.5 | 82 | 82 | 82 | 24 | 24 | 24 | 1 | 1 | 1 | Sample result added to sheet for completeness. Wet weather bypass>10mm - Sample recorded but not reported annually.16mm rainfall. | Added rainfall data. | 2022-05-26
2021-06-03 | 2021-07-08 | 2021-07-13 | 354 | 354 | 354 | 7.2 | 529 | 529 | 529 | 67 | 67 | 67 | 6 | 6 | 6 | Sample result added to sheet for completeness. Wet weather bypass>10mm - Sample recorded but not reported annually 18.9mm rainfall. | Added rainfall data. | 2022-05-26
2021-05-05 | 2021-05-27 | 2021-06-01 | 599 | 599 | 599 | 7.6 | 51 | 51 | 51 | 2 | 2 | 2 | 7 | 7 | 7 | Compliant flow sample for reporting purposes. TSS just above limit. No discharge from site (recycled into process). | Updated comments to provide clarity on compliant sample during discharge. | 2021-06-28
2021-01-29 | 2021-03-25 | 2021-03-25 | 423 | 423 | 423 | 6.8 | 19 | 19 | 19 | 74 | 74 | 74 | 5 | 5 | 5 | 6mm rain on day of sample - compliant result. BOD elevated. No discharge from site. water recycled. | Updated comments to provide clarity on compliant sample during discharge. | 2021-06-28
2020-11-05 | 2021-01-19 | 2021-01-20 | 604 | 604 | 604 | 6.9 | 27 | 27 | 27 | 48 | 48 | 48 | 6 | 6 | 6 | 2mm rain on day of sample - no discharge from site. compliant sample for reporting purposes. BOD slightly elevated. | Updated comments to provide clarity on compliant sample during discharge. | 2021-06-28
2020-10-28 | 2021-01-19 | 2021-01-20 | 498 | 498 | 498 | 6.7 | 40 | 40 | 40 | 78 | 78 | 78 | 4 | 4 | 4 | Sample result added to sheet for completeness. Wet weather bypass>10mm previous 24 hrs - Sample recorded but not reported annually. | Updated comments to provide clarity on compliant sample during discharge. | 2021-06-28
2020-10-07 | 2020-11-14 | 2020-11-23 | 413 | 413 | 413 | 7.1 | 340 | 340 | 340 | 38 | 38 | 38 | 5 | 5 | 5 | 8mm rain prev day and on day of sample. Result driven by turbidity in runoff. | Updated comments to provide clarity on compliant sample during discharge. | 2021-06-28
2020-09-28 | 2021-01-19 | 2021-01-20 | 333 | 333 | 333 | 7.7 | 1090 | 1090 | 1090 | 89 | 89 | 89 | 23 | 23 | 23 | Sample result added to sheet for completeness. Wet weather bypass>10mm previous 24 hrs - Sample recorded but not reported annually. | Updated comments to provide clarity on compliant sample during discharge. | 2021-06-28
2020-08-19 | 2020-11-14 | 2020-11-23 | 228 | 228 | 228 | 6.4 | 48 | 48 | 48 | 6 | 6 | 6 | 5 | 5 | 5 | Rain prev day - compliant sample. Ph sightly lower than limit. | Updated comments to provide clarity on compliant sample during discharge. | 2021-06-28
2020-08-10 | 2020-11-14 | 2020-11-23 | 303 | 303 | 303 | 6.2 | 400 | 400 | 400 | 2 | 2 | 2 | 11 | 11 | 11 | Sample result added to sheet for completeness. Wet weather bypass>10mm previous 24 hrs - Sample recorded but not reported annually. | Updated comments relating to wet weather bypass | 2021-01-19
20/8/20 - Additional column and note added to clarify date sampling data was obtained.
2020-06-01 |  |  | 494 | 494 | 494 | 5.4 | 353 | 353 | 353 | 58 | 58 | 58 | 8 | 8 | 8 | sample taken after extended period of drought. Water recycling has been in effect to reduce load on potable supply.
2020-05-01 | 2020-05-01 | 2021-01-19 | 268 | 268 | 268 | 7.2 | 600 | 600 | 600 | 89 | 89 | 89 | 5 | 5 | 5 | Sample result added to sheet for completeness. Wet weather bypass>10mm previous 24 hrs - Sample recorded but not reported annually.
2020-02-01 |  |  | 251 | 251 | 251 | 6.1 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | sample after consecutive days of light rain.
2020-01-01 |  |  | 246 | 246 | 246 | 7.2 | 2 | 2 | 2 | 22 | 22 | 22 | 4 | 4 | 4 | sample taken after extended period of drought. Water recycling has been in effect to reduce load on potable supply.
2019-09-01 |  |  | 314 | 314 | 314 | 7.2 | 8 | 8 | 8 | 40 | 40 | 40 | 2 | 2 | 2 | Sample collected after 3 months with no rain.
2019-06-01 |  |  | 330 | 330 | 330 | 7.8 | 186 | 186 | 186 | 88 | 88 | 88 | 4 | 4 | 4 | Fist sample for a number of months due to dry conditions. High pollutant load.
2019-03-01 |  |  | 417 | 417 | 417 | 7.7 | 12 | 12 | 12 | 45 | 45 | 45 | 4 | 4 | 4
2018-11-01 |  |  | 679 | 679 | 679 | 7.3 | 122 | 122 | 122 | 52 | 52 | 52 | 4 | 4 | 4
2018-11-01 |  |  | 436 | 436 | 436 | 7.4 | 602 | 602 | 602 | 67 | 67 | 67 | 16 | 16 | 16 | System failure resulting in high pollutant load during discharge.
2018-07-01 |  |  | 639 | 639 | 639 | 7.7 | 21 | 21 | 21 | 114 | 114 | 114 | 8 | 8 | 8
2018-06-01 |  |  | 420 | 420 | 420 | 9.8 | 54 | 54 | 54 | 44 | 44 | 44 | 3 | 3 | 3
2018-05-01 |  |  | 286 | 286 | 286 | 6.9 | 461 | 461 | 461 | 108 | 108 | 108 | 11 | 11 | 11 | TSS levels higher in treated water may indicate sludge separation impacted by blocked TFS filter | Update table to conform with current guidelines | 26/6/2018
2018-02-01 |  |  | 219 | 219 | 219 | 7.9 | 2 | 2 | 2 | See Note |  |  | 1 | 1 | 1 | BOD was unable to be reported due to an interferent present in the sample
2018-01-01 |  |  | 444 | 444 | 444 | 7.7 | 13 | 13 | 13 | 6 | 6 | 6 | 4 | 4 | 4
2017-11-01 |  |  | 345 | 345 | 345 | 7 | 190 | 190 | 190 | 77 | 77 | 77 | 7 | 7 | 7
2017-10-01 |  |  | 467 | 467 | 467 | 6.9 | 14 | 14 | 14 | 45 | 45 | 45 | <1 | <1 | <1
2017-09-01 |  |  | 478 | 478 | 478 | 7.2 | 289 | 289 | 289 | 23 | 23 | 23 | 4 | 4 | 4
2017-08-01 |  |  | 761 | 761 | 761 | 8.7 | 16 | 16 | 16 | 110 | 110 | 110 | 5 | 5 | 5
2017-07-01 |  |  | 994 | 994 | 994 | 10.9 | 11 | 11 | 11 | See note |  |  | 1 | 1 | 1 | BOD was unable to be reported due to an interferent present in the sample
2017-06-01 |  |  | 590 | 590 | 590 | 10.2 | 10 | 10 | 10 |  |  |  | 4 | 4 | 4 | BOD was unable to be reported due to an interferent present in the sample
2017-05-01 |  |  | 1040 | 1040 | 1040 | 10.7 | <2 | <2 | <2 |  |  |  | 2 | 2 | 2 | BOD was unable to be reported due to an interferent present in the sample
2017-04-01 |  |  | 1090 | 1090 | 1090 | 8.8 | <2 | <2 | <2 | 18 | 18 | 18 | 3 | 3 | 3 | Monthly sample taken
2017-03-01 |  |  | 459 | 614 | 770 | 7.4 & 8.8 | 2 | 21.5 | 41 | 17 | 26.5 | 36 | 5 | 5 | 5 | Monthly sample taken - Additional sample taken | Data updated | 2017-06-26
2017-02-01 |  |  | 290 | 290 | 290 | 7.9 | 8 | 8 | 8 | 20 | 20 | 20 | 1 | 1 | 1 | Monthly sample taken
2017-01-01 |  |  | 378 | 378 | 378 | 8.4 | <2 | <2 | <2 | 3 | 3 | 3 | 1 | 1 | 1 | Monthly sample taken | Data updated | 2017-06-26
2016-12-01 |  |  | 990 | 990 | 990 | 9.4 | 9 | 9 | 9 | 22 | 22 | 22 | <1 | <1 | <1 | Monthly sample taken | Sample date | 2017-06-26
2016-10-01 |  |  | 800 | 1030 | 1260 | 9.1 & 9.7 | <2 | 7.5 | 15 | 38 | 44.5 | 51 | 1 | 1.5 | 2 | Monthly sample taken - Additional sample taken | Data updated | 2017-06-26
2016-09-01 |  |  | 673 | 673 | 673 | 8.1 | 15 | 15 | 15 | 39 | 39 | 39 | <1 | <1 | <1 | Monthly sample taken
2016-08-01 |  |  | 383 | 383 | 383 | 7.1 | 17 | 17 | 17 | 144 | 144 | 144 | 6 | 6 | 6 | Monthly sample taken
2016-07-01 |  |  | 280 | 296 | 312 | 6.9 & 7 | 96 | 96 | 96 | 94 | 126 | 159 | 7 | 7.5 | 8 | Monthly sample taken - Additional sample taken | Data updated | 2017-06-26
2016-06-01 |  |  | 569 | 569 | 569 | 7.6 | 267 | 267 | 267 | 109 | 109 | 109 | 5 | 5 | 5 | Monthly sample taken
2016-05-01 |  |  | 255 | 255 | 255 | 7.6 | 28 | 28 | 28 | 25 | 25 | 25 | 4 | 4 | 4 | Monthly sample taken
2016-03-01 |  |  | 221 | 221 | 221 | 8.6 | 7 | 7 | 7 | No data |  |  | 1 | 1 | 1 | No BOD data as laboratory reported an interference substance present.
2016-02-01 |  |  | 280 | 280 | 280 | 8.7 | 5 | 5 | 5 | 8 | 8 | 8 | 4 | 4 | 4 | monthly sample - minor pH NC.
2016-01-01 |  |  | 347 | 375.5 | 404 | 7.3 and 8.1 | 7 | 18.5 | 30 | No data |  |  | 1 | 2 | 3 | No BOD data as laboratory reported an interference substance present in both samples.
2015-12-01 |  |  | 297 | 491.5 | 686 | 8.7 and 7.8 | 4 | 15 | 26 | No data |  |  | 1 | 2.5 | 4 | No BOD data for both samples as laboratory reported an interference substance present in both samples.
2015-11-01 |  |  | 330 | 499 | 668 | 7.8 and 7.7 | 3 | 7 | 11 | No data |  |  | 3 | 3.5 | 4 | No BOD data for both samples as laboratory reported an interference substance present in both samples.
2015-10-01 |  |  | 455 | 502 | 542 | 10, 7.5 and 8.5 | 5 | 14 | 19 | 31.5 | 15 | 48 | 3 | 3 | 3 | Monthly sample taken
2015-09-01 |  |  | 265 | 265 | 265 | 8.1 | 34 | 34 | 34 | 32 | 32 | 32 | 5 | 5 | 5
2015-08-01 |  |  | 261 | 348 | 435 | 7.4 and 9.5 | 47 | 48 | 49 | 103 | 103 | 103 | 6 | 7.5 | 7 | No BOD data for one sample as laboratory reported an interference present in the sample.
2015-07-01 |  |  | 514 | 514 | 514 | 9.7 | 22 | 22 | 22 | 87 | 87 | 87 | 10 | 10 | 10
2015-06-01 |  |  | 724 | 792 | 861 | 10.4 | 5 | 7.5 | 10 | 16 | 43.5 | 71 | 3 | 4 | 5
2015-05-01 |  |  | 639 | 639 | 639 | 9.9 | 19 | 19 | 19 | <2 | <2 | <2 | 1 | 1 | 1 | pH exceeds upper limit of 8.5.
2015-04-01 |  |  | 531 | 531 | 531 | 9.5 | 21 | 21 | 21 | No data |  |  | 2 | 2 | 2 | Lab advised sample contained an interfering substance and could not record a result for BOD. pH exceeds upper limit of 8.5 may be due to presence of interfering substance.
2015-03-01 |  |  | 743 | 743 | 743 | 10.2 | No data |  |  | No data |  |  | 4 | 4 | 4 | Lab advised sample contained an interfering substance and could not record a result for BOD. Lab did not provide result for TSS. pH exceeds upper limit of 8.5 may be due to presence of interfering substance.
2015-02-01 |  |  | 454 | 454 | 454 | 7.8 | 8 | 8 | 8 | 68 | 68 | 68 | 1 | 1 | 1
2015-01-01 |  |  | 405 | 405 | 405 | 7.2 | 4 | 4 | 4 | 8 | 8 | 8 | <1 | <1 | <1
2015-01-01 |  |  | 497 | 497 | 497 | 8 | 12 | 12 | 12 | 5 | 5 | 5 | 1 | 1 | 1
2014-12-01 |  |  | 533 | 533 | 533 | 7.2 | 100 | 100 | 100 | 47 | 47 | 47 | <1 | <1 | <1
2014-10-01 |  |  | 455 | 455 | 455 | 8.5 | 5 | 5 | 5 | 15 | 15 | 15 | 3 | 3 | 3
2014-09-01 |  |  | 655 | 655 | 655 | 9.4 | 118 | 118 | 118 | 220 | 220 | 220 | 17 | 17 | 17
2014-08-01 |  |  | 491 | 491 | 491 | 9.8 | 22 | 22 | 22 | 90 | 90 | 90 | 3 | 3 | 3
2014-08-01 |  |  | 479 | 479 | 479 | 9.8 | 18 | 18 | 18 | 88 | 88 | 88 | 1 | 1 | 1
2014-07-01 |  |  | 590 | 590 | 590 | 8.6 | 32 | 32 | 32 | 106 | 106 | 106 | 2 | 2 | 2